MODELS COVERED: All Selecto filtration systems

- MF6202P (Beverage system 2 carbon filter set) – [Selecto part #: 109-0060] – (set of 2)

- MF620CC (Beverage system 3 carbon filter set) – [Selecto part #: 109-0050] – (set of 3)

- MF620 (Coffee/tea carbon filter) – [Selecto part #: 101-298] – (set of 1)

- CoffeePRO-CF (Coffee/tea scale reduction) – [Selecto part #: 102-160] – (set of 1)

- IcePRO 10 (Ice machine scale reduction) – [Selecto part #: 101-260] – (set of 1)

- 4.5” x 20” Pre-filter (Ice machine/sink sediment filter) – [Selecto part #: 101-231P] – (set of 1)

- 2.5” x 20” Pre-filter (Ice machine/sink sediment filter) – [Selecto part #: 101-233] – (set of 1)

- ScaleOut (Ice machine scale reduction) – [Selecto part #: 101-260] – (set of 1)

COST ESTIMATE: $620–750 per year for filters and labor. (NOTE: Cost could be less for Units that have an older water filtration system.)

- Billing to Unit (net 30). Payable from R&M Account with 12-month Amortization.

MAINTENANCE PERFORMED BY: MainServe

MAINTENANCE ADMINISTRATION PERFORMED BY: Selecto Scientific

Contact Information

Selecto Scientific (800-635-4017)

Task Description

Contract with MainServe calls for MainServe agent to deliver and install complete array of filter cartridges annually based on anniversary date of the last install. In accordance with Selecto specifications, MainServe agent will inspect all filter housings; rinse all sumps and lubricate sump O-rings; replace and flush filter cartridges; inspect/adjust Goulds booster pump for constant 80 psi. In addition, on first visit only, MainServe agent will upgrade IcePRO S-10 or ScaleOut feeder cartridges to 5 lb cartridge and bowl, relocating feeder assembly as necessary to accommodate 5 lb cartridge.

NOTE: If MainServe agent determines that filter system or beverage system requires additional repairs, cost of this additional work will be a Unit expense billed separately from annual filter exchange.

See also SCOPE OF WORK (attached).

*     *     *     *     *     *

NOTE TO OPERATOR: Keep this page and give remaining page(s) to service agent.

Standards

- All maintenance service should be performed according to Selecto specifications.

- Service agent must leave kitchen/mechanical room free of debris and tools.

- Service agent must dispose of used cartridges.

Warnings

Power must be turned OFF at Goulds booster pump disconnect before removing pump controller cover to adjust pressure.

| Goulds booster pump disconnect. | Pump controller. |
| --- | --- |

Steps

NOTE: The following instructions are intended to highlight certain steps in this procedure. Specifications developed by Selecto Scientific may require additional steps.

- Coordinate Unit visit with Operator or manager. Contact Unit at least 48 hours prior to annual visit.

- Confirm with Operator or manager the complete array of cartridges to be replaced prior to visit.

- Inspect all filter housings for cracks and leaks, before placing filter system in bypass in preparation for filter replacement.

Steps (continued)

- Rinse all sumps with mild detergent.

- Lubricate sump O-rings with food grade silicon lubricant.

- Flush all carbon filter cartridges to drain for 4 minutes.

- Upgrade IcePRO S-10 and Scale Out feeder cartridges to 5 lb cartridge and bowl (first visit only). At this time, relocate feeder assembly as necessary to accommodate 5 lb cartridge.

- Inspect/adjust Goulds booster pump for constant 80 psi pressure.

| Pump controller with cover removed. | Filter system inlet gauge. |
| --- | --- |

- Close filter system bypass and return system to normal operation.

Restrictions

- Expected completion date:

- Hours work can be conducted:

- Contractor will attend inspection with Operator/manager:  YES			NO

(Reminder: All changes must be communicated to and approved in advance by Facilities Department and Operator/manager of Unit.)