## Data Collect
SURVEY DATA
Unit # | 1487
Unit Name | The Crossing FSU
Survey Date | 2009-07-08
Filter System Install Date | 2005-10-04
Operator / Manager | Jeff Mosley
Unit Phone # | (317)578-4511
Service Provider Contact Info: Company Name, Contact Name. Contact Phone Primary Technician Technician Phone: | N/A
Service Contract In Place Y or N | No
Service Contract Duration: From xx/xx/09 to xx/xx/09 | N/A
Description of Services & Frequency | N/A
Filtration Components: 4.5 x 20 prefilter, MF620, MF620CC etc. | MF620CC MF620 Bypass Handle with Test Rig Goulds 2A Pump
At least 3.0 Mega Pixel Photos taken using extra lighting:
Last Filter System Service Date | 2008-11-05
Salt Delivery Service Y or N | No- Operator gets salt himself and puts it in
Salt Delivery Service Frequency | they get it every two weeks or so
Last Filter Cartridge Change Date | Culligan PVE-90
Softener Type Culligan / Everpure | 2008-11-05
Softener Has Power / Is turned On Y or N | Yes
Softener In Bypass Y or N | No
Softener Calibrated to Spec Y or N | No
What is out of calibration? | time of day changed from 11:59am to 1:01pm fast rinse changed from 13 min to 11 min
Has resin tank been rebedded? Y or N. If yes, when mm/dd/yy | No
If yes, resin tank rebedding cost? And by whom? | N/A
Salt Level in Brine Tank -Full / 3/4 / 1/2 / 1/4 / Empty | 0.5
Goulds Booster Pump Installed Y or N | Yes
Goulds Booster Pump In Operation Y or N | No
Goulds Pump Plumbed Whole House or Filtered Water Circuit Only | Whole House
Goulds Booster Pump Valves, E, F, D, and D Open Y or N, Describe | Yes
Goulds Booster Pump Controller Status Light Green or Red | Red
Goulds Booster Pump - If Red, What is Status Code (based on # blinks) | 6 blinks- ground fault I cleared the fault by electrically discharging control and now the pump is running well- suspect power surge
Goulds Booster Pump. What is pump running pressure (psi) | 80 psi
Type II Only -What is pressure gauge reading at Tea filter with softener engaged (psi) | 80 psi
Type II Only - What is pressure gauge reading at Tea filter with softener in bypass (psi) | 80 psi
Hardness (ppm) at Beverage Tower | 308 ppm (18 grains)
Hardness (ppm) at Tea Brewer Stop (Type II) or Softener Hose Bibb (Type II or Type III) | 17 ppm (1 grain)
Free Chlorine at Beverage Tower | Not detectable
Total Chlorine at Beverage Tower | Not detectable
Type II Only - Total chlorine at tea brewer stop. | Not detectable
Type II Only - Free chlorine at tea brewer stop. | Not detectable
Type III Only - RO Processor Making Water Y or N | N/A
Type III Only - RO Processor Flow Rate to Holding Tank (gpm) | N/A
Type III Only - RO Processor Permeate Water TDS | N/A
Type III Only - RO Processor Waste Water Flow Rate (gpm) | N/A
Type III Only - RO Processor Waste Water TDS | N/A
Type III Only - Goulds Delivery Pump In Operation Y or N | N/A
Type III Only - Goulds Delivery Pump Controller Status Light Green or Red | N/A
Type III Only - Goulds Delivery Pump. If Red, What is Status Code (based on # blinks) | N/A
Type III Only - Goulds Delivery Pump. What is pump running pressure (psi) | N/A
City Water TDS | 348 ppm
City Water Hardness (ppm) | 308 ppm (18 grains)
City Water Total Chlorine | 1.6 mg/L
City Water Free Chlorine | 1.2 mg/L
Significant Notes About Location | 1. MF620CC filter drain connection is feeding carbonators and non-carb water lines- 5 stubouts abandoned and open at pumps- drain line teed 5 times for carbonator pumps and non-carb water- 2nd line plumbed through bypass is abandoned and open at carbonator pump area- no backflow preventer on carbonator line 2. Ice machine is not filtered 3. Booster pump started up after clearing fault, but had a long loud squeal for a while- it stopped and was not heard again, even after forcing multiple pump starts and stops 4. Operator states that he needs new Tea and Coffee brewers- they are old and torn up, relating to time before store water was softened 5. Dumpster water line severed and not reconnected in mechanical room