TECHNICAL SERVICE REPORT

Water Analysis

| Customer: | Location: | Date: | PO#: |
| --- | --- | --- | --- |
| Chick-fil-A | # 561 | 10/19/05 | 228251 |
| Address: |  | Tested By: |  |
| Boardman Poland Rd. |  | AR |  |
| Phone: | Email: | Selecto Contact: |  |
| 330-726-7205 |  |  |  |

| Recommendation: |  |
| --- | --- |

##### ANALYTICAL RESULTS

| Evaluation of: | Unfiltered Water Sample | Recommended Max Levels |
| --- | --- | --- |
| Fluoride, ppm | 0.7 | 2 ppm |
| Chloride, ppm | 81 | 250 ppm |
| Nitrite, ppm | ND | 1 ppm as N |
| Nitrate, ppm | ND | 10 ppm as N |
| Sulfate, ppm | 334 | 250 ppm |
| Sodium, ppm | 124 | 10 ppm |
| Ammonia as Chloramine | Must be tested on site | .5 ppm |
| Chlorine, ppm | Must be tested on site | Detectable |
| Alkalinity, ppm | 25 | 150 ppm |
| Total Dissolved Solids, ppm | 600 | 500 ppm |
| Hardness, ppm | 208 | 100 ppm |
| pH | 9.2 | 6.5 – 8.5 ppm |
| Turbidity | 0.00 | 0.5 NTU |
| Particle Counts, #/cc | 918 (1-63 micron) |  |

The information supplied is believed to be accurate and is only indicative of the water tested.  The testing laboratory is not state certified.

3980 Lakefield Court    Suwanee, GA 30024    678.475.0799    800.635.4017

www.selectoinc.com

sales@selectoinc.com