TECHNICAL SERVICE REPORT

Water Analysis

| Customer: | Location: | Date: | PO#: |
| --- | --- | --- | --- |
| Chick-fil-A | # 2242 | 11/16/07 | 276968 |
| Address: |  | Tested By: |  |
| NW Corner Ronald Reagan Pkwy Peachtree Pkwy 141 Cumming, GA 30028 |  | AR |  |
| Phone: | Email: | Selecto Contact: |  |

| Recommendation: |  |
| --- | --- |

##### ANALYTICAL RESULTS

| Evaluation of: | T-Mobil Water Sample | Starbuck’s Water Sample | Recommended Max Levels |
| --- | --- | --- | --- |
| Chloride, ppm | 38 | 45 | 250 ppm |
| Sulfate, ppm | 10 | 4 | 250 ppm |
| Sodium, ppm | 48 | 42 | 250 ppm |
| Chloramine | ND | ND | .5 ppm |
| Chlorine, ppm | Detected | Detected | Detectable |
| Alkalinity, ppm | 15 | 10 | 150 ppm |
| Total Dissolved Solids, ppm | 100 | 130 | 500 ppm |
| Hardness, ppm | 20 | 25 | 100 ppm |
| pH | 7.2 | 7.4 | 6.5 – 8.5 ppm |
| Turbidity | 2.0 | 0.00 | .05 NTU |

The information supplied is believed to be accurate and is only indicative of the water tested.  The testing laboratory is not state certified.

3980 Lakefield Court    Suwanee, GA 30024    678.475.0799    800.635.4017

www.selectoinc.com

sales@selectoinc.com